ATV – 131 (Simplified) for a given Constant V

Input Q, X, VT, T, SS0, BOD0, TKNo, NO3o

FT = 1.072T-15

PXT calcs

YobsH=0.75+0.60(SS0BOD0)−0.102((SRT.FT)(1+0.17FTSRT))

PXT=YobsH⋅Q∗BODo

Input T, X

VT=PXT⋅SRTX

VT∗XBODL=0.75+0.60(SS0BOD0)−0.102(SRT.FT)(1+0.17FTSRT)∗SRT

Quadratic Eqn in terms of SRT

Solve for SRT

K=VTX(BODL)

Derived from definition of SRT = VT/PXT and PXT

f1 = 0.102 FT

f2 = 0.17 FT

L=0.75+0.6SS0BOD0

L=0.75+0.6SS0BOD0

a = f2L-f1

b = L –f2K

c = -K

SRT=−b+b2−4ac2a

Analytical solution for CT it is enough to know: T, BOD0, SS0, VT, X given

OUC = 0.56 + 0.15 FT *SRT / (1+0.17 FT *SRT)

POTENTIAL CALC’S

Decreasing nitrification safety factor, increases anoxic volume

Input Nitrification Safety Factor SF=1.45

OURC=BODL∗OUC

VDVT=1−SF∗3.4∗1.10315−TSRT

DNpot calc.

θCA=SF∗3.4∗1.10315−T

Increasing anoxic volume, increases DN-potential DN-pot should not be increased ... are than DNcap

DNpot=a(0.75)(OURC)2.9VDVT

CAPACITY CALC’S

WASN=0.04 BOD0

WASN =0.05 BOD0, if CT < 10d

DNcap calculations

NN=TKNoxid−WASN=TKN0−TKNeff−WASN

Choose TKNeff

DNcap=NDN=NN+(NO3N0−NO3Neff)

Let DNpot = DNcap and solve for NO3Neff

NO3Neff = DNpot /Q – (NN + NO3N0 ) / 1000

Check

If TKNeff + NO3Neff < 10

No

(Select bigger vol)

Yes

YobsH=0.75+0.6(SS0)BOD0−0.102FT∗SRT 1+0.17⋅FT⋅SRT

PXT* = YobsH BODL

X, VT, SRT, VD/VT, NO3Neff

Output

* HSG uses BOD removal load Q(BOD0 – BODeff) # Paşaköy Data T = 14.9 oC MLVSS = 2407 X = MLSS = 5616 CT = 28 d Q = 65 903 m3/d In; effl. COD = 561.83; 561.85; -. BOD = 561.83/2eff; 561.81/2; -. TKN0 = 56.0 – 3.0; 56.0; 3.0. NH4N = 48.2 – 3.4; 48.2; 3.4. NO3N = 0 – 8.9; 0; 8.9.